| Specification Section 32 31 00 FORTRESS VERTICAL LIFT GATE SYSTEM WITH TYM-VSA OPERATOR (ORNAMENTAL) |  |  |
| --- | --- | --- |

GENERAL:

SECTION INCLUDES:

    - The work in this section shall include furnishing all labor, materials, equipment and appliances necessary to complete installation of the Fortress Vertical Lift Gate(s) required for this project in strict accordance with this specification section and drawings.  The Vertical Lift Gate System, including operator and counterbalance weights, shall be specifically designed to complement each other as a system and be provided by a single manufacturer.  Components (operator from one source and gate panel and counterbalance from another) assembled at the job site to form a system will not be approved.

REFERENCES:

    - Underwriters Laboratory Gate Operator Requirements (UL 325).  See 1.03 C-2.

    - ASTM F 2200 Standard Specification for Automated Vehicular Gate Construction.  See 1.03 C-2.

    - American Welding Society AWS D1.2 Structural Welding Code.  See 1.03 C-1.

    - American Welding Society AWS D1.1/D1.1M Structural Welding Code.  See      1.03 C-1.

    - ASTM A 123 Standard Specification for Zinc (Hot-Dip Galvanized) Coatings on Iron and Steel.

    - Current safety standards require gate operators to be designed and labeled for specific usage classes.  Operator Model TYM-VSA is compliant in usage Classes III and IV.

    - American Society of Civil Engineers – ASCE-7 Wind Load Requirements.  See 1.03C4

    - ASCE-7 – Wind Load Requirements (See 1.03 – C3)

SUBMITTALS:

    - Product Data:

      - Provide manufacturer’s catalog cuts with printed specifications and installation instructions.

      - Deliver two (2) copies of operation and maintenance data covering the installed products, including name, address and telephone number of the nearest fully equipped service organization.

    - Shop Drawings:

      - Supply Shop Drawings showing the operating system, including details of all major components.  Include parts list showing manufacturer’s names and part numbers for the complete installation.

      - Include complete details of gate construction, gate height and column spacing dimensions.

    - Certifications:

      - Gate manufacturer shall provide independent certification as to the use of a documented Welding Procedure Specification and Procedure Qualification Records to insure conformance to the AWS D1.2 (aluminum) and AWS D1.1 / D1.1M (steel) Structural Welding Codes.  Upon request, Individual Certificates of Welder Qualification documenting successful completion of the requirements of the AWS D1.2 and AWS D1.1 / D1.1M codes shall also be provided.  See 1.02 C and 1.02 D.

      - Gate manufacturer shall certify gate is manufactured in compliance with           ASTM F 2200, Standard Specification for Automated Vehicular Gate Construction and the operators are UL 325 listed.  See 1.02 B and 1.02 A.

      - Gate is to be designed to meet specified ASCE-7 wind load requirements with the gate in the closed and latched condition only.  Typical gate design is expected to operate satisfactorily in winds up to 30 MPH.  Depending on gate panel infill, winds higher than 30 MPH may cause gate operational problems (operator entrapment sensing may trigger; gate panel may not engage receiver).  For sites with higher operational, non-typical, or specified wind loadings, manufacturer should be advised of the site conditions and a specifically engineered design will be offered.(See 1.02-H)

PRODUCTS:

VERTICAL LIFT GATE SYSTEM MANUFACTURERS:

    - The Vertical Lift Gate System shall be manufactured by Tymetal Corp., 678 Wilbur Avenue, Greenwich, NY 12834 – (800) 328-4283.

    - Approved Substitution – All other systems must be submitted to the design team in accordance with substitution requirements as set forth in the general provisions of the specification manual for approval prior to the bid date.  Products submitted after the bid date will not be approved.

SYSTEM FUNCTION:

    - Operation:

      - System shall be designed so that gate movement from the closed position is impossible except by electric or mechanical means.

    - Rate of Travel:

      - The vertical lift gate operator shall be able to achieve a maximum gate speed of 1.5 ft per second, and shall be equipped with soft-start and soft-stop function to prevent shock load to the gate panel and gate operator.

SYSTEM DIMENSIONS:

    - Clear gate opening HEIGHT shall be: ____ ft-0 in. (               m)

    - Clear gate opening WIDTH shall be:  ____ ft-0 in. (               m)

    - Gate Panel HEIGHT shall be:             ____ ft-0 in. (               m)

    - Gate Panel shall (or shall not) include one additional foot of barbed wire.

TYM-VSA OPERATOR:

    - The TYM-VSA operator is an integral component of the Heavy Duty Vertical Lift Gate system.  This model is adapted to function with most accessories including: radio controls, single and three button control stations, digital keypads, coded cards, sensing loops, telephone entry systems, and revenue control equipment. The operator utilizes 208/230 Volt AC single phase, or 208/230 Volt AC or 460 Volt AC three phase power.  Motor box is 10 gauge galvanized steel with detention grade hinges and mogul lock.

    - The gate operator shall be UL 325 compliant for Class III and IV.

    - The gate operator includes an APeX Controller with integrated radio receiver, plug-in loop detector capability, surge protection, and easy to read labeling standard.

    - Capacity:

      - The gate operator shall be rated to operate a gate weighing up to 4500 lbs.

    - Motor Size:

      - The electrical motor shall be 1 HP, [208/230VAC, Single Phase] or [208/230VAC, Three Phase] or [460 VAC, Three Phase] as produced by a nationally recognized manufacturer.

    - AC Drive:

      - The variable frequency drive unit shall allow for programmable speeds and programmable soft-start and soft-stop features.

    - Overload Protection:

      - Motor shall be protected against overload by either a thermal or a current sensing overload device.

    - Gear (Box) Reducer:

      - The self-enclosed gear-head gearbox shall be manufactured as a single unit, and shall consist of a hardened steel, machine cut worm and mating bronze gear running in oil bath.  The gearbox shall perform the following functions:

        - Adjustable Clutching Device.

        - Manual disconnect by crank handle.

    - Gear Box Heater

      - Operator shall include internal gearbox heater and a heater strip for the control box.

    - Roller Chain:

      - #60 roller chain shall be utilized.

    - Manual Operation:

      - A crank handle, located at ground level in the motor box, shall provide a two-step emergency procedure for manual operation:

        - Unlock and open motor-box door.

        - Fold out handle and crank gate opened or closed.

    - Limits:

      - The operator shall be equipped with an integral limit system, providing accurate settings to control the open and close positions of the gate, and shall not be affected by manual operation or motor removal.

    - Control Circuit:

      - U.L. listed operator shall have 5VDC control signal.

    - Control wiring:

      - The electrical contractor shall supply all exterior control wiring.

    - Audio Alarm:

      - This alarm shall have a dual function.

        - The first function shall be as a warning prior to gate movement.  When the motor control board recognizes a command, this alarm shall be activated three (3) seconds before the motor is energized and the gate begins to move.  This shall be continuously activated while the gate is in motion.

    - Main Power Disconnect Switch and Wiring Compartment:

      - When this switch is in the OFF position, the main power shall be disconnected from the Variable Speed Drive, Motor Control Board and power transformer(s).

    - Transformer:

      - Operators shall have an isolated low voltage (24VDC, 750mA) power supplied to provide power for external control devices (not including external gate lock).

    - Auto Close Timer:

      - The timer provides an automatic closure of the gate from the full open position, adjustable from 0 to 60 seconds.

MOTOR HOUSING:

## Water Resistant Motor Box:

      - The motor box shall be constructed of 10-gauge sheet steel, hot-dip galvanized per ASTM A 123, gasketed and located at ground level for easy maintenance.

    - Security Hinges and Tamper Resistant Security Screws:

      - Security hinges and screws shall be furnished to secure operator enclosure components.

    - Motor Box Lock:

      - Motor box shall be locked with a detention grade dead bolt.  Three (3) keys shall be provided per key code.

ACCESS CONTROL:

## Entrapment Devices:

      - Photoelectric through beams/photo eyes shall be installed to span the clear opening.

    - Optional accessories, contact, non-contact, and control devices:

      - Control devices include pushbuttons, radio controls, keypads, card readers, key switches, telephone entry systems, and revenue control equipment.

      - Contact and non-contact devices include photoelectric sensors, vehicle detectors, proximity sensors, and contact edges.

SAFETY COVER:

    - A safety cover of 16-gauge steel shall house each of the counterweights.

SAFETY DEVICE:

    - A “claw” type safety device shall be provided to stop the gate in the down direction in the event of cable malfunction.

    - Traffic Signal Lights (TS-1 Red/Green) shall be installed on the secure and non-secure side of the gate to control through traffic.  The installation shall be done so that when the gate is in the closed position or moving, the light will be Red to stop traffic.  When the gate is fully open, the light will turn Green to allow through traffic.  A separate 115 VAC power supply is required for the Traffic Signal Lights.

VERTICAL LIFT GATE:

    - System Dimensions:

      - Fortress Vertical Lift Gate System dimensions shall be as shown on the detail drawings.

    - Gate Frame:

      - The gate frames shall be fabricated from 6005A-T61 or 6005A-T5 aluminum alloy extrusions.  The top member shall be a 3” x 5” aluminum structural channel/tube weighing not less than 3.9 lb/lf.  The bottom member shall be a 2” x 5” aluminum structural tube weighing not less than 2.0 lb/lf.  The outside vertical members shall be “P” shaped in cross section weighing not less than 1.6 lb/lf.  Intermediate vertical members shall alternate between 2” x 2” and 1” x 2” in cross section, weighing not less than 1.1 lb/lf and .82 lb/lf respectively.  Intermediates shall be spaced at a maximum of 3’ centers.

    - Track and Trucks:

      - The vertical lift gate shall operate between the flanges of the lifting columns to the required vertical clearance, and shall be held plumb between them by means of four self-aligning, 4-wheeled, ball-bearing truck assemblies and anti-racking cables.  The truck assemblies shall ride in two vertically mounted tracks, extruded from 6005A-T61 or 6005A-T5 aluminum alloy, weighting a minimum of 2.7 lb/lf (4 kg/m).

    - Diagonal Bracing:

      - Diagonal “X” bracing of 1/4” diameter galvanized steel cable shall be installed throughout the gate to provide additional bracing and vertical adjustment.

    - Gate Filler:

      - 1” x 1” aluminum internal or extended smashed point pickets.  To be ASTM F2200 compliant picket spacing should be such that it will prevent a 4 inch diameter sphere from passing through the openings anywhere in the gate panel.

    - Gate Finish:

      - All exposed steel system parts shall be zinc galvanized.

      - Gate panel shall be mill finish aluminum or color coated with polyester powder as specified. If powder coated, the panel shall be pretreated chemically by sand blasting or other acceptable method to ensure proper coating adherence.

STRUCTURAL STEEL COLUMNS:

    - Two W12 x 53 structural steel lifting columns of sufficient height for clearance requirements shall be flanged and fastened to concrete footings with anchor bolts.

ANCHOR BOLTS:

    - Each (2 required per gate) anchor bolt assembly shall consist of four (4) 1 ½” (38 mm) diameter bolts and tie rods for each column, and shall conform to ASTM A-36 grade steel with compatible hexagonal nuts and washers.

CABLE AND BEARINGS:

    - Two 3/8” (9.525 mm) galvanized steel cables, attached to counterweights, shall pass over a 10” (254 mm) diameter sheave located at the top of each column, and shall be fully supported by two of VF-2S-220 Browning pillow block bearings.

WARRANTY:

    - The vertical lift gate and operator system shall be warranted by the manufacturer against manufacturing defects for a period of (3) three years from date of sale.

EXECUTION:

SITE INSPECTION:

    - Final upgrades and installation conditions shall be examined.  Work shall not begin until all unsatisfactory conditions are corrected.

INSTALLATION:

    - Equipment in this section shall be installed in strict accordance with the company’s printed instructions unless otherwise shown on the contact drawings.

    - The complete system shall be adjusted to ensure that it is performing properly.

    - The gate system is to comply with ASTM F 2200 and UL 325.  See 1.02 B and 1.02 A.

    - The installing contractor shall be responsible to ensure that appropriate external primary entrapment safety devices be installed for the specific site conditions to protect against all potential entrapment zones.  Proper operation of these safety devices shall be verified and training as to the operation and maintenance of these devices for the users and owners shall be documented.

SYSTEM VALIDATION:

    - The complete system shall be adjusted to assure it is performing properly.

    - The system shall be operated for a sufficient period of time to determine that the system is in proper working order.

    - System Acceptance Test:

      - The Owner’s Representative shall be notified at least three working days prior to the test so arrangements can be made to have a facility representative witness the test.

      - Test each system function step by step as summarized in controls specification section.

      - Supply all equipment necessary for system adjustment and testing.

    - Test and Explain Safety Features:

      - Each system feature and device is a separate component of the gate system.

      - Read and follow all instructions for each component.

      - Ensure that all instructions for mechanical components, safety devices and the gate operator are available for everyone who will be using the gate system.

      - The warning signs shipped with the gate operator must be installed in prominent position on both sides of the gate.

    - Ensure the owner is clear with regard to the safety points concerning the basic operational guidelines of the safety features of the gate operator system.  These safety points are listed in the operator manual and must be read prior to system use.

Note: Tymetal Corp. reserves the right to modify and/or make changes as deemed necessary without previous notice.