GENERAL:

- 1.01	SECTION INCLUDES:

    - This section covers the furnishing and installation of a TCRB-12-EMLA Crash Rated Beam Vehicle Barrier system.  Provide a complete system that has been fabricated and tested for proper operation at the factory.

    - System includes barrier arm (beam) section, hinge and motor controller with built in receiver buttresses (stanchions), electro-mechanical drive, Motor control unit with built in Programmable Logic Controller (PLC), and safety devices to provide a fully operational barrier system. Overall clear width of barrier arm may be between 10 to 22 feet.

    - Design and materials are identical to those used in the crash test of TCRB-12 and approved by the US Department of State (DOS).

RELATED SECTIONS:

    - Section 03 11 00 Concrete forming

    - Section 03 20 00 Concrete reinforcing

    - Section 28 00 00 Electronic Safety and Security

    - Section 32 31 00 Fencing and Gates

CRASH RATING, TESTING AND QUALITY ASSURANCE:

    - The TCRB-12 crash tested vehicle barrier system has been tested to the requirements of ASTM Standard F-2656-07, standard test method for Vehicular Crash Testing of Perimeter Barriers.  Based on test results the barrier rating per ASTM Standard F-2656-07 is M50-P1* (similar to DOS K-12) in which impact conditions are:

      - Crash Rating:M50-P1

      - Vehicle Weight: 15,000 lbs.

      - Impact Speed: 50 MPH

    - * The clear opening for the tested unit was 18’- 8”.  The unit specified may be of a different clear opening than the tested model but can be expected to perform in a similar manner under similar conditions.

    - The TCRB-12-EMLA crash tested vehicle barrier system MUST be installed per manufacturer’s specifications and designs.  Failure to comply with all installation requirements will void the Crash Rating and Warranty.

    - The TCRB-12 vehicle barrier system has successfully passed an actual crash test and is certified to perform as described in 1.03A above.  A copy of the letter of compliance from the testing agency can be provided upon request.

    - Manufacturer shall be a company specializing in the manufacturing and supply of security vehicle barriers.

- TCRB-12-EMLA Barrier Precautions: Consideration must be given to the selection and placement of vehicle barriers.  Tymetal recommends the use of, but does not provide traffic or safety engineering services.  The TCRB-12 barriers are tested to stop vehicles, and impacts with barriers will result in severe damage to the vehicle.  Approaching vehicles as well as pedestrians must be warned as to the barrier’s presence and operation.  The Owner/Operator of this crash barrier shall assume responsibility for providing traffic and safety engineering, including all necessary safety features to be used at each barrier location, including, but not limited to: sidewalks, roadway lighting, caution signage, traffic lights, audible warning alerts, visual warning alerts, or other traffic control devices and guard booths.  Tymetal recommends an installation configuration that will allow controlled approach speeds.

SUBMITTALS:

    - Submit shop drawings of standard product.

    - Indicate pertinent dimensions, general construction, component connections and location, anchorage methods and location, hardware, and installation details.

DELIVERY, STORAGE AND HANDLING:

    - Deliver material to job site in manufacturer’s packaging undamaged, compete with installation instructions.

    - Store off ground, under cover, protected from weather and construction activities.

PROJECT – SITE CONDITIONS:

    - Install TCRB-12 Crash Rated Beam Vehicle Barrier including excavation, trenching and concrete foundation pads per manufacturer’s printed instructions.

    - Installer/owner to supply required permits/inspections.

WARRANTY:

    - Two (2) years from date of shipment on manufactured components and workmanship.  This warranty excludes normal wear on finishes or damage that occurs due to impact, abuse, misuse or acts of God.

    - Accessories are covered by their manufacturer’s warranty.

    - Warranty is in lieu of all other warranties, expressed or implied, and shall be considered void if visible evidence implies recommended installation procedures and maintenance instructions were not followed.

PRODUCTS:

Vehicle Barrier MANUFACTURER:

    - The vehicle barrier system shall be manufactured to Tymetal Corp. specifications and shall be supplied by Tymetal Corp., 678 Wilber Avenue, Greenwich, NY  12834  -  (800) 328 - 4283.

    - Gate system manufacturer shall be a company specializing in the supply of security vehicle barriers.

    - Gate system manufacturer shall have a minimum of $25 million in liability insurance.

Vehicle BARRIER:

    - The complete TCRB-12-EMLA assembly consists of a receiver stanchion, hinge stanchion, aluminum arm, stanchion covers, and electromechanical power system. This unit was designed using the latest technology in parts and assembly including the use of engineered cables, stainless steel shafts, and details such as self-aligning bearings.

    - Mechanical Components:

      - Power is electromechanical with a heavy-duty linear actuator operated by an electronic variable motor drive, allowing ramped speed operation.

      - The controls will be operated through a programmable logic controller (PLC) capable of providing inputs/outputs to the barrier arm actuator and accessories.

      - Hand Crank: A handle attached to the gearbox allows for manual operation during a power outage.

      - Speed: 10 to 12 seconds to open or close.  Emergency Fast Operation (EFO): Reduction of 1 second.

      - Power Options: 115 VAC or 220/240 VAC single phase, 60 Hz; 220/240 VAC or 460 VAC three phase, 60 Hz; 50 Hz is available.

      - Battery backup is available.

    - Electro-mechanical Components:

      - Power is electromechanical with a heavy-duty linear actuator operated by an electronic variable motor drive, allowing ramped speed operation.

      - The controls will be operated through a programmable logic controller (PLC) capable of providing inputs/outputs to the barrier arm actuator and accessories.

      - Hand Crank: A handle attached to the gearbox allows for manual operation during a power outage.

      - Speed: 10 to 12 seconds to open or close.  Emergency Fast Operation (EFO): Reduction of 1 second.

      - Power Options: 115 VAC or 220/240 VAC single phase, 60 Hz; 220/240 VAC or 460 VAC three phase, 60 Hz; 50 Hz is available.

      - Battery backup is available.

    - Finishes:

      - TCRB-12-EMLA is delivered painted black (buttresses) with a three-part epoxy paint process: First mechanical and then chemical cleaning followed by a high-density zinc primer application and completed with a two-part epoxy paint for corrosion resistance.  Hot dip galvanizing is optional.  Other colors are available, contact manufacturer for details.

      - The beam is finished in stock standard white polyester powder coating and striped with reflective red and white safety tape to increase visibility. The Power Unit is painted industrial gray.

FACTORY INSPECTION AND TESTING:

    - Manufacturer shall test each operator at factory to assure smooth, quiet operation.

    - Manufacturer shall test all control inputs to ensure proper function.

EXECUTION:

Site Inspection:

    - Examine final grades and installation conditions.

    - Installer must examine the location and advise the Contractor/Owner of any site conditions unacceptable for proper installation of product.  The conditions include but are not limited to the following:

      - Existing underground utilities or unforeseen issues.

      - Removal of pavers, stones road surfaces or landscaping.

    - Do not begin work until all unsatisfactory conditions are corrected.

Installation:

    - Install equipment of this section in strict accordance with the company’s printed instructions.

    - Buttress Installation: The hinge and receiver buttress are cast in a concrete foundation below grade.

    - Set units level and plumb and in line with adjacent structures or roadway.  Anchor securely into place.

    - Use installers with experience in the installation of vehicle barriers.  For a list of qualified installers please contact manufacturer.

System Acceptance & validation:

    - Acceptance Test:

      - Test each system function.

      - Installer should adjust beam arm, hardware and sensors for smooth operation and proper performance.

    - Test and Explain Safety Features:

      - Ensure that the owners and operator of the barrier is clear on the electrical disconnection and safe manual operation of the unit.

      - Ensure that all instructions for mechanical components, safety devices and installed accessories are available for everyone who will be operating the vehicle barrier system.

    - System Validation:

      - The complete system shall be adjusted to assure it is performing properly.

      - The system shall be operated for a sufficient period of time to determine that the system is in proper working order (typically 30 cycles or 36 hrs)

      - Ensure the owner is clear with regard to the safety points concerning the basic operational guidelines of the vehicle barrier system.

      - Installer and customer shall complete Post Installation Check Off Sheet

Note: Tymetal Corp. reserves the right to modify and/or make changes as deemed necessary without previous notice.